## Case E1
229 Reference Table | Requirement | Work-around | Issue
Table 6 | Air Film Resistance | OS/E+ determines the air film resistances dynam ically, for each timestep. | Table 6: Interior Air Film Resistance Summary was unable to be implemented. E1.7.2.3.1 d, The exterior air-film resistance for roof and exterior walls was unable to be implemented
Table 13 | Auxiliary Heat Lockout Temp 4.4°C (40°F) | The electric backup heating coil will operate at temperatuires > 40F if the capacity provided by the DX hearing coil cannot meat the htg load. | Connot model an Auxiliary Heat Coil Lockout Temp of 4.4°C (40°F), without requiring an E+ EMS program to be developed | 4.4°C (40°F)
Table 13 | Energy Recovery Leaving Air Temp Control shall be "Fixed Setpoint" | The Enthalpy wheen will recover as much energy from the exhaust air stream as possible using a enthalpy wheel with a 50% effecitveness | Energy Recovery Leaving Air Temp Control defined as "Fixed Setpoint", but no "Fixed Setpoint" value provided in the spec.

## Case E2
229 Reference Table | Requirement | Work-around | Issue
14A | Supply Air Temp Control | Implemented "Warmest Zone" Supply Air Reset Strategy | Zone Reset – 15.6°C (60°F) at minimum load

## Case E3
229 Reference Table | Requirement | Work-around | Issue
Table 15 A unable to meet requirement Terminal 2 Type - Air distribution effectiveness

## Case F110
229 Reference Table | Requirement | Work-around | Issue
12A | Minimum Outdoor Air = 600 CFM | Model PTHP with 600 cfm OA, when operating | It is uncommon tp HAV PTHP systems with a variable outside air capability (modulating OA dampers) . OpenStudio/EnergyPlus, PTHP ZoneHVAC Equipment Systens are not allowed to have fans that are variable flow - they can use the FanOnOff object but only at a single fan flow.
12A | Maximum Outdoor Air = 2000 CFM | Model PTHP with 600 cfm OA, when operating | In OpenStudio/EnergyPlus, PTHP ZoneHVAC Equipment Systens are not allowed to have fans that are variable flow - they can use the FanOnOff object but only at a single fan flow.
12A | Auxiliary Heat Type | Model PTHP with electric | Can be handled with an OS measure
12A | Cooling Efficiency, Full Load | Model Using 12.3 IEER = 3.35 Rated COP | No defendable conversion from IEER to Rated COP is known. Used COP = (IEER / 10.75) / 3.413

## Case F140
229 Reference Table | Requirement | Work-around | Issue
15A | 11.0 CEER | Assumed that this was an error, should be 11.0 EER setting COP to 3.51 | Combined Energy Efficiency Ratio (CEER) is a measure of how energy efficient a room air conditioner is, Not the efficiency of a DX Cooling coil inside a packaged commercial HVAC Unit.
15A | Terminal Type: Variable Volume | Modeled each zone as using a "EnergyPlus AirTerminal:SingleDuct:ParallelPIU:Reheat" object | The spec requires each terminal unit be a "parallel fan-powered box" vaving variable air flow. EnergyPlus/OS does supprt a parallel fan powered box terminal unit that operates in this manner.

## Case F150
229 Reference Table | Requirement | Work-around | Issue
16A | 0.5 NPLV | Use Air Cooled Chiller COP = 4.1 | I am unaware of a standard method for converting a chiller NPLV value into a rated COP value + set of associated performance curves.
16A | Terminal Type: Variable Volume | Modeled each zone as using a "EnergyPlus AirTerminal:SingleDuct:ParallelPIU:Reheat" object | The spec requires each terminal unit be a "parallel fan-powered box" vaving variable air flow. EnergyPlus/OS does supprt a parallel fan powered box terminal unit that operates in this manner.
16B | Heat Rejection Fan Control: Two Speed | Modeled as "Chiller:Electric:EIR" with a condensor fan power ratio == 0 | EnergyPlus/OpenStudio does not support the modeling the energy performance of an Air Cooled Chiller that has two speed condenser fan.

## Case F160
229 Reference Table | Requirement | Work-around | Issue

## Case F170
229 Reference Table | Requirement | Work-around | Issue

## Case F180
229 Reference Table | Requirement | Work-around | Issue
19B | 0.5 NPLV | Use Air Cooled Chiller COP = 4.1 | I am unaware of a standard method for converting a chiller NPLV value into a rated COP value + set of associated performance curves.

## Case F190
229 Reference Table | Requirement | Work-around | Issue
20B | Chiller Part Load Efficiency: 0.5 NPLV | Use Water Cooled Chiller COP = 4.1 | I am unaware of a standard method for converting a chiller NPLV value into a rated COP value + set of associated performance curves.